## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.15 Testing for electrotechnical systems
PowerPoint: 1.15 Continuity
Notes: Use guidance note 3 to assist in the delivery of this PowerPoint.

## Slide 2: Introduction
What is continuity?

## Slide 3: Objectives
By the end of this session, you should be able to:
Identify the correct test instruments and settings for measuring continuity of protective conductors
Describe methods for verifying continuity of bonding, earthing, CPCs and ring final circuit conductors

## Slide 4: Regulation 643.2.1
Regulation 643.2.1 requires that a continuity check be carried out on all protective conductors. This includes the earthing conductor, the protective conductors of all circuits, all main protective bonding conductors and, where applicable, all supplementary bonding conductors.
Regulation 643.2.1 also requires a continuity check is carried out on each conductor of every ring final circuit, including the line, neutral and protective conductors.

## Slide 5: Verify continuity of protective bonding conductors
Verifying the continuity of the bonding conductors ensures that all metalwork within the installation is at the same potential.
When exposed and extraneous conductive parts have the same potential, fault currents will not flow between them.

## Slide 6: Verify continuity of earthing conductors
The reason for verifying continuity of the earthing conductor is to ensure there is a connection to the main source of earthing, either supplied via the distributors facility (TN system) or by an earth electrode (TT system).

## Slide 7: Verify continuity of circuit protective conductors
Verifying the continuity of the CPC of every circuit ensures there is a path of low resistance, allowing a fault current to flow safely to earth. This will reduce the risk of electric shock.
If the CPC's resistance was lower than yours, then the majority of the high fault current would flow through the lowest resistance by ratio and ensure that a protective device would operate very quickly.
If no CPC is present, then under a fault condition, you may be the lowest resistance path, and the current would flow through your body to earth, resulting in an electric shock.

## Slide 8: Verify continuity of ring final circuit conductors
This test is required to verify the continuity of each conductor, including the CPC, in every ring final circuit.
This is to ensure there are not two radial circuits instead of a ring circuit fed from a 32 amp protective device when wired using 2.5mm2 cable.
The test will also identify the presence of any loose connections and whether the ring has been interconnected to create an apparent continuous ring, with spurs feeding spurs. This is verified by a three-step test approach, as explained in GN3.

## Slide 9: Methods to check protective conductor continuity
Test method 1 uses the circuit Line and CPC conductors connected at the distribution board, measuring the R1+R2 value.
Test method 2 uses a supplementary length of test cable (the “wandering lead” method), measuring the R2 value.
The instrument used for low-resistance tests may be either:
a specialised low-resistance ohmmeter or
the continuity range of an insulation and continuity tester.
All instruments used must comply to BS EN61557.
Notes: State and say that the results of either test method are recorded on the schedule of test results.

## Slide 10: Results
The results should first and foremost indicate no discontinuity in the protective conductors.
For lengths of conductor, use Appendix B of Guidance Note 3 for resistance data.
For joints across bonds by earth clamps and similar, the readings should approach 0.05Ω, taking into account the resolution of the instrument, its accuracy at low values and contact resistance.
Notes: https://engx.theiet.org/f/wiring-and-regulations/30536/bonding-maximum-resistance
Show image of GN3 Figure 2.16: The image shows the test being conducted with the bonding conductor still terminated in the distribution board, it's best practice to disconnect the bonding conductor for the test to avoid parallel paths affecting the test results.

## Slide 11: Using test method 1
When conducting this test, ensure that the link is removed before energising the installation.
Use a temporary link, connected between line and earth in the distribution board.
This measured value confirms continuity of both the line and earthing conductor. It is the circuit’s R1+R2 value, which is measured at each outlet.

## Slide 12: Using test method 2
Account should be taken of the possibility of test readings being affected by parallel paths, so carry out the test with the protective conductor disconnected at one end.
Main switch OFF and safely locked off. Disconnect the bonding conductors at the main earth terminal only. Place one lead on disconnected bonding conductor and the other on the metallic pipe near the bonding clamp. Then do the same for all the other bonds where applicable. A long wander lead may be needed.
Set dial on Continuity range and take the measurement after zeroing the meter leads or taking their resistance into account. Reconnect the bonding conductors once the test is complete.
This test confirms continuity of the CPC which is the R2 test value.
Notes: This method is usually only used on bonding conductors as a separate test would be required for dead polarity if this method was used for circuits.

## Slide 13: Method for ring final circuit conductor continuity
This is a three-step test to verify the continuity of the line, neutral and protective conductors and the correct wiring of every ring final circuit.
Step 1: Verifying the continuity of the line conductors
Step 2: Verifying there are no interconnections within the ring
Step 3: Verifying true R1+R2 value of the ring circuit

## Slide 14: Step 1
This test verifies the continuity of the line conductors.
Measure the end-to-end resistance of the line conductor.
Image supplied by www.test-meter.co.uk.
E1 N1 L1 L2 N2 E2
0.6 Ω
Low-resistance ohmmeter

## Slide 15: Step 1 continued
Measure the end-to-end resistance of the neutral conductor.
All measured values taken between the ends of line and neutral conductors should be within 0.05Ω of each other or further investigation will be required.
E1 N1 L1 L2 N2 E2
0.6 Ω
Low-resistance ohmmeter

## Slide 16: Step 1 continued
E1 N1 L1 L2 N2 E2
1.0 Ω
Low-resistance ohmmeter

## Slide 17: How to verify CPC measurement
This measured value of the CPC should be 1.67 times greater than either the line or neutral end measurement.
This is the case when a 1.5mm² earth is used in conjunction with a 2.5mm² Line conductor.
i.e. 2.5/1.5 = 1.67 mm²
1.67 is the ratio difference between the two sizes of conductors, which affects the resistance value by the same ratio.

## Slide 18: Step 2
This test verifies that there are no interconnections within the ring and no spurs off spurs.
All measured values taken on each socket outlet must be within 0.05Ω of each other, or further investigation will be required.
It is important that the links are connected in the correct way.
0.3 Ω

## Slide 19: Step 3
The highest value recorded on any socket will be the true R1+R2 value of the ring circuit.
All measured values taken on each socket outlet must be within 0.05Ω of each other, or further investigation will be required.
0.4 Ω

## Slide 20: Polarity
On completion of the ring circuit test, polarity can be taken as correct.
There will be no need to test polarity again.
This is the only process in which polarity is automatically checked as correct once the ring circuit has been tested and all results are satisfactory.

## Slide 21: Calculated values explained for ring circuit testing
If the r1 and rn values from step 1 were each measured at 0.6 Ω then the expected value between L and N at each socket at step 2 would be 0.3 Ω (see calculation below).
To calculate the expected value, we take the loops from step 1, add them together and then divide by four, for example, 0.6 + 0.6 = 1.2 / 4 = 0.3Ω
Note: if spurs are installed, this value will be higher.

## Slide 22: Calculated values continued
r1 was 0.6 Ω and r2 was 1.0 Ω then R1+R2 would be verified as 0.4 Ω (see calculation below).
To calculate the expected value, we take the loops from step 1, add then together and divide by four, for example, 0.6 + 1.0 = 1.6 / 4 = 0.4Ω
Note: if there are spurs installed, then this value will be higher. The highest value recorded will be the R1+R2 of the circuit.

## Slide 23: Summary
You should now be able to:
Identify the correct test instruments and settings for measuring continuity of protective conductors
Describe methods for verifying continuity of bonding, earthing, CPCs and ring final circuit conductors

## Slide 24
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.